## Summary-1
Compliance monitoring and fulfilment of VJV2013 Specifications concerning of Power Classes 2, 3 and 4
Printed | 2026-08-05
Specifications concerning Power Generating Facility | VJV2013
Production type
Rated capacity
Type of Turbine Generator(s)
Location and VJV Reference point
Commissioning
VJV2013 process status
Situation 2014-01-22 | Not started | Started | Shall be specified/ corrected | Accepted | Comments
Requested and granted deviations from VJV2013 Specifications | x
Specification of VJV Reference Point | x
Delivery of general Power Generating Facility data | x
Delivery of project-specific Power Generating Facility data | x
Planning of Compliance Testing | x
Accepted performance of Compliance Testing, and documentation of Compliance Testing | x
Acceptance of the compliance monitoring process of the Specifications | x
Compliance monitoring process of VJV2013 Specifications | Compliance monitoring and documentation obligation concerning the VJV2013 Specifications has not been fulfilled, process in progress

## S1
Data to be delivered |  | Related item in VJV2007 | A request for a report related to the VJV2013 Specifications has been sent | Data related to the VJV2013 Specifications has been successfully delivered | Status of data exchange related to potential deviations and/or the Specifications | Comments
1 | Basic data, structure and location of Power Generating Facility |  |  |  | Accepted
2 | Reactive Power capacity calculation |  |  |  | Accepted
3 | Technical details of Turbine Generators |  |  |  | Accepted
4 | Active Power control and Frequency Control |  |  |  | Accepted
5 | Reactive Power control and voltage control |  |  |  | Accepted
6 | Frequency operating range and voltage operating range |  |  |  | Accepted
7 | Calculation of the operation of the Power Generating Facility during momentary voltage disturbance, and potential reports of factory testing |  |  |  | Accepted
8 | Description of the fault current injection of the Power Generating Facility during voltage disturbance, and power restoration after voltage disturbance |  |  |  | Accepted
9 | Data on the transformers and main components of the Power Generating Facility |  |  |  | Accepted
10 | General data or simulation models required for the modelling of the operation of the Power Generating Facility |  |  |  | Accepted
11 | Required specific studies related to the Specifications |  |  |  | Accepted
12 | Real-time measurement data |  |  |  | Accepted
13 | Preliminary schedule of Power Generating Facility project |  |  |  | Accepted
Status of stage 1 |  |  |  | Accepted

## S2
Data to be delivered |  | Related item in VJV2007 | A request for a report related to the VJV2013 Specifications has been sent by Fingrid | A request for a report related to the VJV2013 Specifications has been accepted | Status of data exchange related to potential deviations and/or the Specifications | Comments
1 | Further specifications to the data presented in stage 1 |  |  |  | In progress
2 | Protection settings of Power Generating Facility |  |  |  | In progress
3 | Power quality |  |  |  | In progress
4 | Project-specific data on Active Power control and Frequency Control |  |  |  | In progress
5 | Project-specific data on Reactive Power control and voltage control |  |  |  | In progress
6 | Project-specific data or simulation models required by the modelling of dynamic operation |  |  |  | In progress
7 | Preliminary commissioning schedule and commissioning programme |  |  |  | In progress
K
Status of stage 2 |  |  |  | In progress

## S3-S
Test |  | Availability of functionality has been verified | Operation in accordance with the Specifications has been verified | Status | Comments
1 | Operation at Minimum Output |  |  | Must be renewed
2 | Reactive Power capacity |  |  | Must be renewed
3 | Step response of voltage control of generator |  |  | Must be renewed
4 | Constant voltage control |  |  | Must be renewed
5 | Functioning of underexcitation limiter |  |  | Must be renewed
6 | Functioning of overexcitation limiter |  |  | Must be renewed
7 | Functioning of power system stabiliser (PSS) |  |  | Must be renewed
8 | Response of Frequency Control to normal frequency fluctuation |  |  | Must be renewed
9 | Response of Frequency Control to step-like and ramp-like changes |  |  | Must be renewed
10 | Dead band of Frequency Control |  |  | Must be renewed
11 | Transitions in the modes of power control and Frequency Control |  |  | Must be renewed
12 | Restriction and rate of change of power |  |  | Must be renewed
13 | Transition to house load operation, remaining in house load operation |  |  | Must be renewed
14 | Fault ride-through |  |  | Must be renewed
Status of stage 3 |  | Must be renewed

## S3-W
Test |  | Availability of functionality has been verified | Operation in accordance with the Specifications has been verified | Status | Comments
1 | Operation at Minimum Capacity |  |  | Must be renewed
2 | Start-up of Power Generating Facility |  |  | Must be renewed
3 | Reactive Power capacity |  |  | Must be renewed
4 | Constant Reactive Power control |  |  | Must be renewed
5 | Constant power factor control |  |  | Must be renewed
6 | Constant voltage control |  |  | Must be renewed
7 | Transitions between Control Modes |  |  | Must be renewed
8 | Active power curtailment |  |  | Must be renewed
9 | Restriction of rate of change of active power |  |  | Must be renewed
10 | High wind operation |  |  | Must be renewed
11 | Rapid downward control of active power |  |  | Must be renewed
12 | Frequency Control |  |  | Must be renewed
13 | Transitions between Control Modes |  |  | Must be renewed
14 | Power quality |  |  | Must be renewed
15 | Fault ride-through |  |  | Must be renewed
Status of stage 3 |  | Must be renewed

## S4
VJV2013 sub-entity, and data to be delivered in stage 4 | Action started | Action performed in an accepted manner | Status | Comments
Further specifications to the data presented in stages 1 and 2
Stage 1
Stage 2
Stage 3
Commissioning report and required results in Numerical format
Validated modelling data or simulation models needed in modelling of the Power Generating Facility
Final set values of controllers of Power Generating Facility/generators
Final set values of protection of Power Generating Facility/generators
Compliance monitoring | Accepted